|  | Please check the following points before contacting us. Thank you. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Headings | Customer |  |  |  |  |  |  |  |  |  | Contact |  |  |  |  |  |  | Tel.No. |  |  |  |  |  |
|  | Error description |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | When did the problem occur? |  |  |  |  |  |  |  |  |  |  |  | How long is plant already in operation? |  |  |  |  |  |  |  |  |  |  |
|  | Fan Art.No. |  |  |  |  |  |  |  |  |  |  |  | Fan type |  |  |  |  |  |  |  |  |  |  |
|  | Number of incorrect fans / total fans |  |  |  |  |  |  |  |  |  |  |  | Serial number motor |  |  |  |  |  |  |  |  |  |  |
|  | Order number |  |  |  |  |  |  |  |  |  |  |  | Motor PPA-Nr. |  |  |  |  |  |  |  |  |  |  |
|  | Site |  |  |  |  |  |  |  |  |  |  |  | Application (e.g. kitchen) |  |  |  |  |  |  |  |  |  |  |
|  | Finished Troubleshooting from the manual? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Y  |  | N  |
| Electrical | Electrical testing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Did you check the power supply directly on the fan? (3 phase) |  |  |  |  | Polarity and voltage of set point OK? (0 > X < +11VDC) |  |  |  | Could you measure the 24 V and 10 V voltage output from the fan? |  |  | No parallel wiring between 24 V and 10 V in multiple fans systems |  |  |  | Could you analyze the fan with ECParam over RS485? (PC / Connection / Converter) |  |  |  |  | miscellaneous: |  |
|  | Y  | N  |  |  |  | Y  |  | N  |  | Y  |  | N  | Y  | N  |  |  | Y  |  | N  |  |  |  |  |
|  | Questions about the electrical connection (Power Supply) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Test minimal configuration (Set point, Enable, see manual)? |  |  |  |  | Power supply from public network (TN-net)? |  |  |  | Correct power supply? According to Type plate? |  |  | Grounding of fan complete and correct? |  |  |  | Control voltage is laid in a separately cable? |  |  |  |  | Any high voltage testing’s made from customer? |  |
|  | Y  | N  |  |  |  | Y  |  | N  |  | Y  |  | N  | Y  | N  |  |  | Y  |  | N  |  |  | Y  | N  |
|  | Questions about the electrical connection (Control Voltage) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Operating mode / Circuit diagram Nr. |  |  |  |  | Set point 0-10 V DC (incl. GND) |  |  |  | Voltage between external GND and PE <15 V |  |  | Voltage supply for Enable from |  |  |  | Voltage on open contact, alarm relay? |  |  |  |  | miscellaneous: |  |
|  | Control-, Regulation-, Bus mode |  |  |  |  | Poti External 4-20 mA … |  |  |  | Y  |  | N  | fan 24 VDC external 24 VDC … |  |  |  | U= |  | Voltage ACDC |  |  |  |  |
| Mechanical | Questions for the application |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | AHU manufacturer |  |  |  |  | Type of installation |  |  |  | Clean and non-aggressive air (i.e. no kitchen exhaust, dust) |  |  | Airstream temperature < value on name plate |  |  |  | Space for Air-Out-Flow > 1,5*D Impeller Ø |  |  |  |  | Space for Air-In-Flow > 0,5*D Impeller Ø |  |
|  | Ros |  |  |  |  | Inside | Outside |  |  | Y  |  | N  | Y  | N  |  |  | Y  |  | N  |  |  | Y  | N  |
|  | Installation of the fan  Electronic |  |  |  |  |  |  |  |  | Built in components |  |  |  |  |  |  | Humidity < 95 % |  |  |  |  | miscellaneous: |  |
|  | above | lateral |  |  |  | below |  |  |  | Heat recovery |  | Bypass | Heater | Chiller |  |  | Y  |  | N  |  |  |  |  |
|  | Questions about the tightness of the electrical connection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable gland firmly applied |  |  |  |  | Terminal area lid firmly applied |  |  |  | No dirt or cable remains below the lid |  |  | original cable gland |  |  |  | Flat sealing on gland present |  |  |  |  | miscellaneous: |  |
|  | Y  | N  |  |  |  | Y  |  | N  |  | Y  |  | N  | Y  | N  |  |  | Y  |  | N  |  |  |  |  |
|  | Questions to the fan |  |  |  |  |  |  |  |  | Extended Support (Remote Diagnosis)  EC-support@rosenberg-gmbh.com |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Fan Sound levels |  |  |  |  | Packaging OK |  |  |  | 1) This sheet filled out completely. |  |  | 2) Images (fan name plate, motor name plate, Electrical connection, Installation situation, Application, Wiring diagram…) |  |  |  | 3) Connect ECParam via a USB-RS485 Converter (H55-00054) and read out the Parameter-File and save a Log file if possible. |  |  |  |  | 4) If possible provide a video of the fan failure behavior. |  |
|  | Bearing damage Unbalance Balancing weights Grinding noises Transport damage … |  |  |  |  | Yes Damaged Wet … |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Conclusion | Accomplished Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | No actions necessary |  |  |  |  | Correct the connecting |  |  |  | ECParam |  |  | Flashing Firmware |  |  |  | Change electronic |  |  |  |  | Replace the fan |  |
|  | Other |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Date: _______________ Signature (legible): ________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |